## Event Timeline
timestamp_pacific | operational_state | operational_state_name | event | command | result | voltage_rms | current_rms | real_power | reactive_power | apparent_power | power_factor | accumulated_volume_gal | flow_gpm | hot_temp_c | hot_temp_f | cold_temp_c | cold_temp_f | ambient_temp_c | ambient_temp_f
2026-08-10T19:09:44.741-07:00 | [5 empty] | 120.848 | 0 | 2.314 | 6.942 | 8.099 | 0.285
2026-08-10T19:09:44.827-07:00 |  |  | controller_started | controller | started
2026-08-10T19:09:44.831-07:00 |  |  | serial_open | serial_port | ok
2026-08-10T19:09:44.832-07:00 |  |  | communication_started | cta2045 | started
2026-08-10T19:09:45.148-07:00 |  |  | command_sent | outside_communication | pending
2026-08-10T19:09:48.300-07:00 |  |  | incomplete_message | unknown | error
2026-08-10T19:09:48.341-07:00 |  |  | command_completed | outside_communication | timeout
2026-08-10T19:09:48.914-07:00 | 11 | Idle, opted out | operational_state | query_operational_state | received
2026-08-10T19:10:00.959-07:00 |  |  | command_sent | advanced_load_up | pending
2026-08-10T19:10:01.225-07:00 |  |  | command_completed | advanced_load_up | ok
2026-08-10T19:10:15.406-07:00 | 6 | Idle Heightened | operational_state | query_operational_state | received
2026-08-10T19:10:46.009-07:00 | 6 | Idle Heightened | operational_state | query_operational_state | received
2026-08-10T19:11:03.182-07:00 | [5 empty] | 120.858 | 0.179 | 20.826 | 24.297 | 32.396 | 0.643
2026-08-10T19:11:08.211-07:00 | [5 empty] | 120.858 | 0.292 | 32.396 | 34.709 | 48.593 | 0.69
2026-08-10T19:11:16.259-07:00 | 3 | Running Heightened | operational_state | query_operational_state | received
2026-08-10T19:11:40.383-07:00 | [5 empty] | 118.733 | 27.482 | 2867.003 | 2266.529 | 3656.065 | 0.784
2026-08-10T19:11:41.390-07:00 | [5 empty] | 120.799 | 2.156 | 291.56 | 82.146 | 303.129 | 0.961
2026-08-10T19:11:42.396-07:00 | [5 empty] | 120.76 | 2.486 | 335.525 | 78.675 | 344.781 | 0.973
2026-08-10T19:11:43.403-07:00 | [5 empty] | 120.819 | 2.672 | 356.351 | 96.03 | 367.921 | 0.968
2026-08-10T19:11:44.409-07:00 | [5 empty] | 120.741 | 2.991 | 402.63 | 91.402 | 413.043 | 0.975
2026-08-10T19:11:45.416-07:00 | [5 empty] | 120.76 | 2.815 | 379.49 | 83.303 | 388.746 | 0.976
2026-08-10T19:11:45.854-07:00 | 3 | Running Heightened | operational_state | query_operational_state | received
2026-08-10T19:11:48.434-07:00 | [5 empty] | 120.604 | 2.937 | 393.374 | 90.245 | 402.63 | 0.974
2026-08-10T19:11:52.458-07:00 | [5 empty] | 120.692 | 3.045 | 409.572 | 92.559 | 419.985 | 0.975
2026-08-10T19:11:54.470-07:00 | [5 empty] | 120.76 | 3.179 | 428.084 | 94.873 | 438.496 | 0.976
2026-08-10T19:12:00.114-07:00 |  |  | command_sent | run_normal | pending
2026-08-10T19:12:00.309-07:00 |  |  | command_completed | run_normal | ok
2026-08-10T19:12:02.476-07:00 | 1 | Running Normal | operational_state | query_operational_state | received
2026-08-10T19:12:02.516-07:00 |  |  | controller_stopped | controller | stopped

## Device Information
timestamp_pacific | opcode1 | opcode2 | response_code | response_name | payload_length | cta2045_version_raw_hex | cta2045_version | cta2045_b_version_valid | vendor_id_hex | device_type_hex | device_type_name | device_revision_hex | capability_bitmap_hex | model_number | model_number_supported | serial_number_redacted | serial_number_supported | firmware_year_raw | firmware_month_raw | firmware_day_raw | firmware_date | firmware_major | firmware_minor
2026-08-10 19:09:45 | 1 | 129 | 0 | success | 48 | 4200 | B | true | 0x0118 | 0x0003 | Water Heater - Heat Pump | 0506 | 000001C0 | HPTV-50 | true | 136865*** | true

## Master Schedule
enabled | event_id | time_after_start | phase | event_type | action | event_duration_minutes | advanced_value | advanced_units | expected_operational_states | target_volume_gal | expected_flow_gpm | notes | advanced_efficiency
TRUE | advanced_load_up_1 | 00:00:00 | pre_event | cta | advanced_load_up | unknown | 5 | 100_wh | 3¦6
TRUE | test_end | 00:02:00 | recovery | test | end

## Commodity Summary
metric | value
cumulative_electricity_start_Wh | 367251
cumulative_electricity_end_Wh | 367251
cumulative_electricity_change_Wh | 0
total_energy_storage_Wh | 2202
present_energy_storage_start_Wh | 120
present_energy_storage_end_Wh | 120
present_energy_storage_minimum_Wh | 90
present_energy_storage_maximum_Wh | 120
advanced_total_energy_storage_Wh | 2412
advanced_present_energy_storage_start_Wh | 330
advanced_present_energy_storage_end_Wh | 120
advanced_present_energy_storage_minimum_Wh | 90
advanced_present_energy_storage_maximum_Wh | 330